## Slide 2: 3-1297 Burner Management System with DeltaV SIS Charms
May 2025

## Slide 3
LUIZ CLAUDIO
Instrumentation Coordinator / Samarco
THIAGO MACHADO
Automation Engineer / Samarco
TIAGO CORONA
Business Development Manager / Emerson

## Slide 4: Samarco Mineração SA
Samarco Mineração is a Brazilian mining company founded in 1977 and since 2001 controlled through a joint venture between Vale S.A. and Anglo-Australian BHP Billiton, each with 50% of the company's shares. The area had its concession transferred from Sociedade Anônima Mineradora Trindade to Samarco.

## Slide 6
47 YEARS OF
Joint venture
VALE + BHP
Innovation in low-grade ore mining
400 km Pipeline
2nd largest in the transoceanic market (2025)
Capacity to produce
30 million tons of pellets
Among the largest exporters in Brazil
PORT
PELLETIZING
Producer of high-grade iron ore pellets (Fe > 67%)
history
EXTRACTION
BENEFICIATION
PIPELINE

## Slide 7
FROM MINAS TO ESPÍRITO SANTO
Offices
BRAZIL
NETHERLANDS
MG
ES
MARIANA
OURO PRETO
(Germano's operations)
ANCHIETA
(Ubu operational unit and port terminal)
BELO HORIZONTE
(Central officel)
50%
50%
Samarco
SINGAPORE
Notes: Samarco has three pipelines, with 395km. The iron ore pulp travels around three days, at approximately 6km/h, from the Germano Complex to the Ubu Complex, crossing 25 cities from Minas Gerais to Espírito Santo.

## Slide 8
PRODUCTIVE PROCESS - OVERVIEW
FROM START TO END OF PRODUCTION
Mine and Buffer Pile
1
Conveyor Belt - TCLD
2
Screening and Crushing
3
Stock Pile
4
Grinding, Desliming and Flotation
5
Thickening and Storage Tank
6
Sandy Tailings Filtation
7*
PDER - Waste and Tailings Disposal Pile - South
8*
Alegria Sul Pit
9*
Pump and Pipeline Station
10
Gravity Tower
11
Thickening and Homogenization Tank
12
Ore Filtration
13
Pulp Basin
14
Industrial Effluent Treatment Station - ETEI
15
Roller Press
16
Grinding and Mixing
17
Pelletizing
18
Electrostatic Precipitators
19
Hardening furnace
20
Screening
21
Storage Yards
22
Wind Fence
23
Port
24
* The disposal of tailings includes pit and dry staking, without the use of a dam.
GERMANO COMPLEX IN MINAS GERAIS
UBU COMPLEX IN ESPÍRITO SANTO

## Slide 9
SUSTAINABILITY GUIDELINES
DECARBONIZATION
WASTE AND TAILINGS
BIODIVERSITY
WATER
Zero waste in landfills;
Operate without tailings dams;
Fully meet the GISTM standard.
Have a positive impact (“Net Positive Impact”) on the biodiversity of the biomes in which we operate.
Achieve zero net emissions by 2050.
Reduce new water intake and generate a positive impact on the basins where we operate.

## Slide 10: Adequacy of the BMS Combustion System of the 3ª Pelletizing Plant.
May 2025

## Slide 11
BMS - Burner Management System’
Current situation:
BMS panel designed and manufactured by KEI TEK is used in plants 1, 2 and 3. Assembled with contactors without safety classification for combustion systems, they are not adherent to national and international standards (NFPA85, NFPA86, NBR12313, IEC61508, IEC 61511), and are currently completely deteriorated and need to be recovered respecting the national and international standards applied to SIS and natural gas combustion systems operating at low and high temperatures.
Most panels are unavailable, requiring 100% replacement of internal contactors.
Premises:
Adapt the combustion control system, in compliance with regulatory standards;
Use panels with cooling to increase the useful life of the components.
Maximize the use of existing resources;
Proposal: Adequacy of the safety instrumented system (SIS) for combustion control of the furnace of plant 3 (BMS).
Standardized solution with plant 4 and adhering to NBR 12313, IEC 61511, NFPA85 and NFPA86 standards.
Demobilization of obsolete BMS panels, assembly of new panels, testing and commissioning.
Assembly of the new panels, tests and commissioning.
Hardware SIS, DeltaV.
Main Risks
Delivery time of materials
High temperature in the burner walkway as in Plant 4.
Moment 2 – Automation / Instrumentation Scope

## Slide 12
BMS - Burner Management System
References of standards demonstrating the need for a safety instrumented system
SIS – Safety Instrumented System
Parallel and independent to the process control system
Moment 2 – Automation / Instrumentation Scope

## Slide 13
BMS - Burner Management System
References of standards demonstrating the need for a safety instrumented system
Trecho da NBR12313 – 2000
A partir da IEC 61508 calcula-se o SIL das malhas de segurança do processo
Moment 2 – Automation / Instrumentation Scope

## Slide 14
Furnace 3 - Combustion System
NON-CONFORMITIES
Control logic outside the requirements of national and international standards.
Components in need of technological updating
Advanced degree of oxidation of the panels
Unidentified components in the area
Lack of documentation to meet the requirements of the standard
Instruments not suitable for gas application
AGGRAVATING
Difficulty in maintaining the system and difficulty in diagnosing failures, due to the use of relay logics.
Standards Applied to Industrial Plants
Status Atual
Current System – NOT COMPLYING WITH STANDARDS
NBR 12313
Control and safety for the use of combustible gases in low and high temperature processes
NFPA 86
Standard for Ovens and Furnaces
NFPA 85
Boiler and
Combustion
Systems Hazards
Code
IEC 61511 + IEC 61508
Process Industry Safety Instrumented System Standards
Moment 2 – Automation / Instrumentation Scope

## Slide 15
Gas rack and old BMS panel

## Slide 16
Gas rack and old bms panel
GAS RACK – FURNACE 3
ENTRY GAS
BLOQUEIO
MANUAL
REDUCTOR PRESSURE
OVERPRESSURE
PSL LOW PRESSURE SWITCH
VALVES LOCK - NF
VALVE VENT - NA
VALVE CONTROL
BUBBLER
PSH PRESSURE SWITCH DE HIGH
REDUCTOR PILOT
PSL PILOT
PSH
PILOT
BLOCK
PILOT
VALVES LOCK - NF
PANEL OF COMMAND BMS
BURNER
DOUBLE RACK

## Slide 17
Forno 3 - Sistema de Combustão - REENGENHARIA
System fully adherent to the standards applied to industrial plants with natural gas operation Programming logic and control strategies, integrated in a single automation system Controller with integrated safety function and I/O modules with intrinsic safety certification – SIL 2 Revised documentation
Expected Results
Total Cost – R$ 9 million
Moment 2 – Automation / Instrumentation Scope

## Slide 18
Inclusion of the Pressure Reduction Skid in the DeltaV SIS in Specific Panel
- 464 pontos
- 930 pontos
LOCAL CONTROL PANEL Signals will not be included in the DeltaV SIS
BMS – USINA 3 – DELTAV SIS
Natural gas operation only. Oil operation maintained without modifications to DELTAV
+ 44 pontos
Risk Analysis of the Non-Migration of the Oil Combustion System to the SIS
INTERCONNECTION PHILOSOPHY
Double redundancy withdrawal from the SZ controller
BMS panels powered by uninterruptible voltage
Moment 2 – Automation / Instrumentation Scope

## Slide 19
Architectural drawing

## Slide 20: Interconnection philosophy
Reduction Skid Pressure
BMS-113
BMS-113

## Slide 21
Natural gás pressure reduction, flow measurement and blockage station - U03-06RG107.

## Slide 22
State and transition matrix

## Slide 23
306-BMS-113 – Pressure reduction station control and flow measurement

## Slide 24
Third Pellet Hardening Furnace

## Slide 25
Burner management
Notes: Adicionar tela geral do Forno

## Slide 26
Burner fuel selection and general controls

## Slide 27
Combustion system management and ignition sequence

## Slide 28
Management of the combustion system and ignition sequence of each burner
It follows in yellow, which conditions the flame sensor of the main burner is used.
PILOT INTERLOCKS
High Pressure in the Pilot Low Pilot Pressure Pilot's Flame Loss (Ionization) Actuated Emergency Pushbutton Main Burner Failure. Burner Not Enabled Seq. Primary
GAS PRINCIPAL INTERLOCKS
High Gas Pressure Low Gas Pressure Flame Loss Below 760 ºC. Actuated Emergency Pushbutton Undetected Gas Lance Pilot Off and Temp. Below Auto Ignition Failure Closure Vent Valve. Failure Opening Inlet Valve Failure Closing Outlet Valve Unselected Gas V4/5/6 Low Speed and DP4/5/6 Closed and Off Low Heat. V1 and DP V1 and Out of Low Fire Position. High Burner Temperature 1400ºC Trip Section. Burner Not Enabled Seq. Primary
PILOT PERMISSIVES
Early Flame on Pilot (Ionization) Gas Selected and Without Permission Consecutive Burner Failure Time Early Flame on Main Burner
PERMISSIVES OF THE GAS PRINCIPAL
Low Fire Position Vlv. Control Unselected Gas Undetected Gas Lance

## Slide 29
Flame sensor main burner
DURAG Flame Sensor Tests
Flame Sensor Installation Local
Sensor Durag D-LX 201 M5
Notes: A norma diz que precisamos de ter o monitoramento contínuo da chama do queimador principal independente da do queimador Piloto e de outros queimadores do forno enquanto estivermos abaixo de 760ºC, Este sensor faz a distinção da chama através da diferença de intensidade e frequência da chama do queimador principal e Piloto.
Verificar na lógica se realmente é apenas abaixo de 760C

## Slide 30
New BMS Panel – Deltav SIS
1 BMS for every 4 gas burners
1 Local control panel for each 2 gas burners

## Slide 31
Panel BMS – DeltaV SIS

## Slide 32
Standardized solution with plant 4 and adhering to NBR 12313, IEC 61511, NFPA85 and NFPA86 standards; Demobilization of obsolete BMS panels, assembly of new panels, testing and commissioning; Labor for engineering the configuration of the system, reduced due to similarity with plant 4; Assembly of the new panels, tests and commissioning; SIS, DeltaV hardware identical to that of plant 4; 20 km of control, power and network cables. 8,336 I/O wire connections.
Total: 43.219Hrs
Adequacy of the combustion system of the plant 3 - BMS

## Slide 33
Revitalization of the pressure reduction stand; Revitalization of the burner stands; Acquisition and Installation, calibration and commissioning of new instruments (~1100 Instruments and actuators); Revitalization of all field infrastructure. Development of engineering documentation. Development of logics TAF of logics. Commissioning. Assisted operation.
Adequacy of the combustion system of the plant 3 - BMS

## Slide 34
Conclusion
Benefits/Gains:
  Increased productivity: Because the greater availability of the plant increases productivity. Increased lifespan of equipment: SIS helps to increase the lifespan of equipment and systems. Risk reduction: SIS helps reduce the risk of accidents, such as fires, explosions, damage to the equipment, among others. Protection of personal health: SIS helps to avoid risks to personal health. Increased combustion system availability. Improved combustion system diagnostics. Operational Return of Plant 3.
Adequacy of the combustion system of the plant 3 - BMS

## Slide 35
On the eve of its 47th anniversary, on August 24, Samarco will start operating two Pellet Plants at the Ubu Complex, in Espírito Santo. The reactivation of the plant known as P3 is another step towards the consolidation of the company's business plan to reach 60% of its production capacity by the end of the year, operating in a safer and more sustainable way.
The resumption of P3 was scheduled for January 2025, but was brought forward to operate with the surplus ore from the Pelletizing Plant, known as P4, optimizing production processes. Currently, the company operates at 30% of capacity, equivalent to about 9 million tons of iron ore pellets and fines per year. Since the resumption in December 2020 until July this year, 30.7 million tons were produced. The forecast is to reach 100% by 2028.
Renato Casagrande, Governor of the State of Espirito Santo turning on the pelletizing plant
Operational return of plant 3
Notes: Às vésperas de completar 47 anos, no dia 24 de agosto, a Samarco passa a operar com duas Usinas de Pelotização no Complexo de Ubu, no Espírito Santo. A reativação da usina conhecida como P3 é mais um passo para a consolidação do plano de negócios da empresa para alcançar 60% da sua capacidade produtiva até o final do ano, operando de forma mais segura e sustentável.
A retomada da P3 estava prevista para Janeiro de 2025, mas foi antecipada para operar com o excedente de minério da Usina de Pelotização, conhecida como P4, otimizando processos de produção. Atualmente, a empresa opera com 30% da capacidade, o equivalente a cerca de 9 milhões de toneladas de pelotas e finos de minério de ferro por ano. Desde a retomada, em dezembro de 2020, até julho deste ano, foram produzidas 30,7 milhões de toneladas. A previsão é atingir os 100% até 2028.

## Slide 36
START OF OPERATION PLANT 3
Agosto/2024
EARLY MONTHS
5
Resultados
Main Budget Impacts: (4,7 BRL MM): Increase in costs with return and incorporation of FP and transportation of inputs. (3,6 BRL MM): Increase in operating service costs. (7 BRL MM): 12% increase in workforce costs (Samarco). (2 BRL MM): Growth in matrix costs, especially restaurants. (17,5 BRL MM): Increased maintenance costs. Benefits Achieved: 18,3 BRL MM de Savings in thermal cost from October. 82,7 BRL MM ou 13,7 MM de dólares Increase in net revenue with an increase in production: 806 ktms more pellets in the year (+9.33%). Quality improvement: Increase of 4.5% in the compression parameter of the pellets produced with the entry of Plant 3. Estimated financial return of: 66,2 BLR MM 1 Dollar = 6,04 Reais brasileiro
M2
Anticipation results – under validation
Notes: M2 – Momento 2